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PIT Weekend Change Summary



17 November 2007


Conference Call Number / Code: N/A

Paul Haynes


Desk: +44 (0)207 500 4972



SAN BAU

Carl Williams 


Mobile: +44 (0)7966 466 956



SAN Projects & Integration

1. Tools Needed

· Laptop

· Serial Cable

2. Access Requests

	09191072
	PENDING
	EUDCSMA
	INFORM
	11/17/07
	ACCESS REQUIRED TO SECURE FLOOR - RDC


3. Connectrix Cabinet decommissioning – RDC4

	09151333
	APPROVED
	EUDSPI
	3DAY
	11/17/07
	POWER OFF CONNECTRIX CABINET - BU26 RDC4

	09151327
	APPROVED
	EUDSPI
	3DAY
	11/17/07
	POWER OFF CONNECTRIX CABINET - BU18 RDC4


a. For each Connectrix cabinets BU18 and BU26

i. SAN PIT – Power down  old switches 07/08R

ii. CRS - Power off PDU supplies

iii. CRS - Unplug underfloor commando sockets, and remove cables

iv. SAN PIT - Raise Connectrix cabinet stabilising feet, and roll cabinet back

v. CRS - Replace cut tile with whole tile

b. No Back out is required – Powering off Decommissioned switches

4. Commission Test lab Connectrix Cabinets and SW01/02 – RDC3

	09151263
	APPROVED
	EUDSPI
	3DAY
	11/17/07
	COMMISSION TEST LAB SAN CAB & SWITCH01 - RDC3

	09151284
	APPROVED
	EUDSPI
	3DAY
	11/17/07
	COMMISSION TEST LAB SAN CAB & SWITCH02 - RDC3


a. For each Connectrix cabinets Z03/Z43

i. SAN Pit - Roll back EC1500 cabinet

ii. CRS - Place cut tile at location

iii. CRS - Plug underfloor power cables to commando socket

iv. CRS - Turn on PDU feed to supplies

v. SAN PIT - Bring UTP/fibre cabling into cabinet

vi. SAN PIT - Power up SAN switches

vii. SAN PIT – Configure basic switch settings – see Appendix A

a. IP Addressing

b. Domain ID, Gateway, Mask

viii. SAN PIT – Connect Fibre and UTP

ix. SAN PIT - Discover Switches on SAN service processors

x. SAN Pit – Carry out advanced switch settings – See Appendix B

a. Upgrade EOS

b. Standard Set up config

xi. Oliver Cabling – Provide SAN patches from Core to New Edge – See Appendix B

b. No Back out is required as test lab is not being connected to production SAN

5. Commission SAN Switches 21/22R – RDC3

	09146700
	APPROVED
	EUDSPI
	3DAY
	11/17/07
	INSTALL NEW RED FABRIC SAN SWITCH - RDC3

	09146721
	APPROVED
	EUDSPI
	3DAY
	11/17/07
	INSTALL NEW BLUE FABRIC SAN SWITCH - RDC3


a. For Each SAN switch

i. SAN PIT – Configure basic switch settings – see Appendix A

a. IP Addressing

b. Domain ID, Gateway, Mask

ii. SAN PIT – Connect Fibre and UTP

iii. SAN PIT - Discover Switches on SAN service processors

iv. SAN Pit – Carry out advanced switch settings – See Appendix A

a. Upgrade EOS

b. Standard Set up config

v. Oliver Cabling – Provide SAN patches from Core to New Edge – See Appendix B

6. Appendix A


	Action
	Switch Name - SW21R_EDGE_RDC3
	Switch Name - swrdctestlab01
	Comments

	
	
	
	

	Location
	RDC3-Z03
	RDC3-Z03
	 

	DOMAIN ID
	25
	1
	 

	IP ADDRESS
	169.186.198.135
	169.186.198.140
	 

	Default G/W
	169.186.198.129
	169.186.198.129
	 

	Mask
	255.255.255.192
	255.255.255.192
	 

	Sofware level
	09.00.00 76
	09.00.00 76
	 

	Switch Priority
	Never Principle
	Never Principle
	 

	Interop Mode
	McData Fabric 1.0
	McData Fabric 1.0
	 

	Speed Setting
	1GIG
	1GIG
	 

	Email Alert
	ON
	ON
	 

	Threshold Alert
	ON @ 90%
	ON @ 90%
	san.support@imceu.eu.ssmb

	SNMP
	DISABLED
	DISABLED
	 

	TELNET
	DISABLED
	DISABLED
	 

	WEBSERVER
	DISABLED
	DISABLED
	 

	Nickname
	SW21R_EDGE_RED_RDC3
	SW01_TL_RDC3
	 

	
	
	
	

	Action
	Switch Name - SW22R_EDGE_RDC3
	Switch Name - rdctestlab02
	Comments

	
	
	
	

	Location
	RDC3 - Z42
	RDC3 - Z42
	 

	DOMAIN ID
	25
	1
	 

	IP ADDRESS
	169.186.198.136
	169.186.198.141
	 

	Default G/W
	169.186.198.129
	169.186.198.129
	 

	Mask
	255.255.255.192
	255.255.255.192
	 

	Sofware level
	09.00.00 76
	09.00.00 76
	 

	Switch Priority
	Principle Never
	Principle Never
	 

	Interop Mode
	McData Fabric 1.0
	McData Fabric 1.0
	 

	Speed Setting
	2GIG
	2GIG
	 

	Email Alert
	ON
	ON
	 

	Threshold Alert
	ON @ 90%
	ON @ 90%
	san.support@imceu.eu.ssmb

	SNMP
	DISABLED
	DISABLED
	 

	TELNET
	DISABLED
	DISABLED
	 

	WEBSERVER
	DISABLED
	DISABLED
	 

	Nickname
	SW22R_EDGE_BLUE_RDC3
	SW02_TL_RDC3
	 


7. Appendix B

	Fibre Patching Schedule
	 
	End to End

	SW_Port
	-
	Fibre Panel
	>>
	Fibre Panel
	-
	SW_Port
	 
	CORE Switch_Port
	 
	EDGE Switch_Port

	SW15R_0
	-
	RDC4-RDC3-##
	>>
	RDC4-RDC3-##
	-
	SW21R_0
	 
	SW15R_0
	-
	SW21R_0

	SW15R_4
	-
	RDC4-RDC3-##
	>>
	RDC4-RDC3-##
	-
	SW21R_4
	 
	SW15R_4
	-
	SW21R_4

	SW15R_8
	-
	RDC4-RDC3-##
	>>
	RDC4-RDC3-##
	-
	SW21R_8
	 
	SW15R_8
	-
	SW21R_8

	SW15R_15
	-
	RDC4-RDC3-##
	>>
	RDC4-RDC3-##
	-
	SW21R_15
	 
	SW15R_15
	-
	SW21R_15

	SW15R_20
	-
	RDC4-RDC3-##
	>>
	RDC4-RDC3-##
	-
	SW21R_20
	 
	SW15R_20
	-
	SW21R_20

	SW15R_24
	-
	RDC4-RDC3-##
	>>
	RDC4-RDC3-##
	-
	SW21R_24
	 
	SW15R_24
	-
	SW21R_24

	SW_Port
	-
	Fibre Panel
	>>
	Fibre Panel
	-
	SW_Port
	 
	CORE Switch_Port
	 
	EDGE Switch_Port

	SW16R_0
	-
	RDC4-RDC3-##
	>>
	RDC4-RDC3-##
	-
	SW22R_0
	 
	SW16R_0
	-
	SW22R_0

	SW16R_4
	-
	RDC4-RDC3-##
	>>
	RDC4-RDC3-##
	-
	SW22R_4
	 
	SW16R_4
	-
	SW22R_4

	SW16R_8
	-
	RDC4-RDC3-##
	>>
	RDC4-RDC3-##
	-
	SW22R_8
	 
	SW16R_8
	-
	SW22R_8

	SW16R_15
	-
	RDC4-RDC3-##
	>>
	RDC4-RDC3-##
	-
	SW22R_15
	 
	SW16R_15
	-
	SW22R_15

	SW16R_20
	-
	RDC4-RDC3-##
	>>
	RDC4-RDC3-##
	-
	SW22R_20
	 
	SW16R_20
	-
	SW22R_20

	SW16R_24
	-
	RDC4-RDC3-##
	>>
	RDC4-RDC3-##
	-
	SW22R_24
	 
	SW16R_24
	-
	SW22R_24


8. E-Mail: *GT EU TI Capital Markets Leads when complete with changes
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