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Plan for: Weekend 15th January 2005 

Consisting of 4 Items
Item1: Items brought forward from previous installations – Covered by change control numbers:

1-1: CR05089731

1-2: CR05089731

1-3: CR05089731

1-4: CR05014390

Work co-ordinator: David Coles

Item2: Break/Fix snagging - Covered by EMS reference:

EMS17999

Work co-ordinator: David Coles

Item3: 150105-01 – Covered by change control number:05260070

Work co-ordinator: Graham Rodell

Item4: 150101-02 – Covered by change control number:05265282

Work co-ordinator: Paul Haynes

Locations:
TR1/TR2

CGC2 3rd floor

RDC 1st floor

RDC 4th floor

Conference Call Number: 0207 986 7934 (pin 7934)
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Version Control

	Date
	Version
	Reason for Change

	10/01/05
	Weekend150105_V02
	Re-formatting of layout to reflect recommended changes, and standard appendixes.

Insertion of Break/fix snagging, and Drawings

	11/01/05
	Weekend150105_v1.0
	Addition of: DMX details to appendix B, insertion of appendix F, Details of FCO remediation, details of items carried forward and break/fix snagging

	12/01/05
	Weekend150105_v1.1
	Changes as highlighted at the 14:00 meeting 11/01/05 – Additional sign off section, appendix G and typo’s

	13/01/05
	Weekend150105_v1.2
	Addition of Chris Hankinson’s details

	17/01/05
	Weekend150105_v1.3
	Sign off draft


Documentation Changes

Changes to be reflected in the documentation after successful completion of the whole of this work plan are as follows:

Connectrix service processors names will now be: 

For RDC:

Blue Fabric
rdcbluefabric full DNS name rdcbluefabric.eur.nsroot.net IPAddress  169.186.192.197

Black Fabric

rdcblackfabric full DNS name rdcblackfabric.eur.nsroot.net IPAddress 169.186.192.196
For CGC

Blue Fabric
cgcbluefabric full DNS name cgcbluefabric.eur.nsroot.net IPAddress 169.186.141.197 
Documentation changes (continued)

Email names will be:

For RDC

Blue Fabric

EmailFromAddress=Connectrix-service.RDC.BLUE@rdcbluefabric.eur.nsroot.net
Black Fabric

mailto:EmailFromAddress=Connectrix-service.RDC.BLACK@rdcblackfabric.eur.nsroot.net
For CGC

Blue Fabric

EmailFromAddress=Connectrix-service.CGC.BLUE@cgcbluefabric.eur.nsroot.net
As per appendix E

	Documentation update Sign Off: 2 Pages – To be returned to BAU on completion

Member of: _____________ 

NAME: ____________________ 

Date: __/__/____


Overview of All Weekend Work

Item1: Issues brought forward that require weekend activity.

4 Items brought forward that require weekend activity – please see Item1 for full details

Item2: Break/Fix Snagging

1 Item requires weekend activity – Please see Item 2 for full details

Item3: Upgrade and relocation of laptop service processors to 1U service processors – Blue/Black Zone RDC and CGC1/2.

The following contains the details of the work to be undertaken over the weekend of the 15th of January 2005 at the Citigroup CGC1 TR1/TR2, CGC2 and RDC 1st and 4th floor sites:

The upgrade and relocation of laptop service processors to 1U cabinet mounted service processors will consist of the following three steps:
1) Pre-requisites checks to ensure: 

· There is one connection installed from each 1U service processor to the CEP firewall.

· The Modem lines, and modems are in place for the 1U service processors.

· The CEP firewall on the 4th floor RDC is configured and ready for the installation on the 15th January 2005.
2) The Upgrade and relocation will consist of the following:

· Disconnecting existing laptop service processors. 

· Connecting the new 1U Service Processor’s to the CEP firewall 

· Reconfiguring the new Service Processor’s IP address, default Gateway, Subnet Mask and config.properties
· Test email to confirm dial home and that the installation is complete.
3) Post checks to make sure that the Management Work station are capable of communicating with the Service Processors.

Item4: Remediation of power supply cabling and labels- DMX 5R and 6R 

Without interruption to service Data Centre staff assisted by ENC CS and Applied Engineering will transpose Aux A and Aux B power cables for DMX5R and 6R.located at RDC Level 1

Required Resource 
Resources presence required: 

	MEMBER OF
	CGC RESOURCE
	RDC RESOURCE

	EMC CE
	Patrick Caborn
	Patrick Caborn

	EMC TS
	Tahir Shahid
	Tahir Shahid

	OLIVER CABLING
	Carl Williams
	Carl Williams

	BUSINESS AS USUAL
	David Coles
	David Coles

	BUSINESS AS USUAL
	Paul Haynes
	Paul Haynes

	APPLIED ENGINEERING
	Graham Rodell
	Graham Rodell

	EMC Project Manager
	Gary Battersby
	Gary Battersby

	EMC SAM
	Paul Belcher
	Paul Belcher

	Citigroup Electrician
	Not allocated until 15/01/05
	Not allocated until 15/01/05

	Citigroup Tile Lifter
	Not allocated until 15/01/05
	Not allocated until 15/01/05


This work is the first of 2 steps in migrating the existing ‘laptop’ service processors to 1U service processors, whilst ensuring the connections behind the firewall.

This document is to be used as a complement of the official project document and not as substitute.

Over All Sign Off

	Item
	Status
	Owner
	Sign off



	Item 1: Items brought forward from previous installations
	Items 1-1, 1-2 & 1-4 Completed – Item 1-3 carried over as stated.
	BAU – David Coles
	

	Item 2: Break/Fix Snagging
	Item 2-1 – Complete
	BAU – David Coles
	

	Item 3: Upgrade and relocation of laptop service processors to 1U service processors
	Incomplete - Black SP in RDC was relocated from 1st to 4th floors. Blue zone was not moved in CGC or RDC as there are no modem lines in the new 1U cabinet – Blue SP’s are carried over to the 29/01/2005.
	Applied Engineering – Graham Rodell
	

	Item 4: Remediation of power supply cabling and labels- DMX 5R &6R


	Incomplete – Spare Power supply was not cabled to the PDU so remediation could not go ahead – Rescheduled for 22/01/05.
	BAU – Paul Haynes
	


	Overall Sign Off: 1 Page – To be returned to BAU on completion

Member of: _____________ 

NAME: ____________________ 

Date: __/__/____


Item 1: Items brought forward from previous installations

4 ITEMS BROUGHT FORWARD

	Item  number
	Reference
	Description
	Prerequisites
	Comments
	Resolution

	1-1
	CR-5089731
	Creation of pairs on SYMM 122 to 200
	
	See Appendix F
	Complete DC

	1-2
	CR-5089731
	Unblock ports for the new Fa’s on SYMM 122
	
	See Appendix F
	Complete DC

	1-3
	CR-5089731
	Unblocking of ISL between Switch1C and 7C Port 22.

Fabric rebuild
	
	To be carried over to 22nd of January 2005
	

	1-4
	CR-05014390
	Investigation of ISL issue between rdfsw92r and rdc94r Port 20.

Replacement GBIC 
	
	Port 20 on RDFSW92R & RDFSW94R are blocked because they are streaming bit error threshold exceeded errors.  We should try remediate this following our normal procedures.


	Complete DC


	Item1 Sign Off: 1 Page – To be returned to BAU on completion

Member of: _____________ 

NAME: ____________________ 

Date: __/__/____


Item 2: Break/Fix Snagging

	Item Number
	VT/EMS Reference
	Description
	Comments
	Resolution

	2-1
	EMS: 17999
	Unblocking of an ISL between 2R and 12R.

Fabric rebuild
	A four port card in SWITCH 2R  failed & was swapped out.  One of the cables was an ISL to SWITCH 12R.  This needs unblocking – it is port 28.
	Complete DC


	Item2 Sign Off: 1 Page - To be returned to BAU on completion

Member of: _____________ 

NAME: ____________________ 

Date: __/__/____


Item 3: Upgrade and relocation of laptop service processors to 1U service processors:

Blue Zone in CGC1/2 

Blue and Black Zones in RDC
Work number: 150105-1

Change control number:05260070

Work co-ordinator: Graham Rodell

Date: 

15th of January 2005

Location:
TR1/TR2

CGC2 3rd floor

RDC 1st floor

RDC 4th floor

Conference Call Number: 0207 986 7934 (pin 7934)

Item 3: Section Checklist

Upgrade and relocation of laptop service processors to 1U service processors

	Section
	Details
	Comments
	Sign Off

	3-1
	Pre-requisites checks.
	Checks were carried out as detailed in section 3-1. 
	 



	3-2
	Upgrade and relocation of Blue/Black service processors.
	No analogue DEL’s were available for the Blue Service Processors – CGC/RDC – these moves have been carried over to the next available installation cycle – 29/01/05.

Relocation of active Black service processor proceeded as planned.
	 

	3-3
	Post checks.
	BAU Post checks were carried out as detailed in section 3-3. Oliver cabling did not de-patch the connections, as EMC TS shut down the original service processor – This was deemed easier for a rollback scenario.
	

	3-4
	Post Activity
	Post activity was carried out as detailed in section 3-4.
	 

	Item 3 completion Sign Off: To be returned to BAU on completion.

Member of: _____________________________ NAME: ___________________________________ Date: ___/___/____




Section 3-1: Pre-requisites checks
	Step
	Time
	Owner
	Details
	Comment
	Date Due

	1
	Before starting:
15th of January 2005
	Applied Engineering
	Applied engineering will confirm via email that the firewall configuration is setup and functioning successfully as per appendix C


	Applied engineering has received confirmation that the configuration is set up, but this can not be tested, until installation.
	11/01/2005

	2
	Before starting:
15th of January 2005
	Oliver Cabling
	Oliver Cabling should confirm that there is a connection available for each of the cabinet locations that will be connected to the firewall, as per appendix D


	Survey was carried out on Saturday 08/01/2005 – connections are available in all locations.
	11/01/2005

	3
	Before starting:
15th of January 2005
	Applied engineering
	Applied engineering will confirm there are available Modems and modem lines in the new service processor cabinets.


	VR42020 was raised for temporary installation of 4 analogue extensions, and the installation of 4 x DEL lines. (Extensions to be removed after DEL’s installed) This is still awaiting approval – Installation for the 15th January 2005 is unlikely. The DCSM team also advised they required more leadtime for the RS232 installations. The Modem lines for the BlackZones in RDC are in the cabinets RDC4.
	 11/01/2005


Section 3-2: Upgrade and relocation of Blue/Black service processors
	Step
	Time
	Owner
	Details
	Comment



	1
	When section 

3-1 is confirmed and completed. 15th January 2005
	EMC TS
	EMC TS will follow the appendix D and set the IP address, default Gateway and Subnet Mask for each connectrix service processor as required.


	Un connected service processors may be configured prior to 14:00 – 15th January 2005

	2
	
	EMC TS
	EMC TS will follow the appendix D and amend the config.properties file in the EFCM folder on each connectrix service processor as per appendix E


	Un connected service processors may be configured prior to 14:00 – 15th January 2005

	3
	
	EMC TS 
	EMC TS will apply the access client restriction for all 4 management workstation for each service processors. (By IP) – As per appendix D

169.183.26.108 – (eusan-mgt1)

169.186.223.81 – (eusan-mgt2)

169.183.27.90 – (eusan-mgt3)

169.186.223.170 – (eusan-mgt4)
	Un connected service processors may be configured prior to 14:00 – 15th January 2005

	4
	14:00 – 15th January 2005
	BAU
	Prior to the Upgrade and relocation work, BAU Will commence weekend zoning work at 14:00.


	BAU will contact Oliver cabling (Via conference line) once zoning is complete.


Section 3-2: Upgrade and relocation of Blue/Black service processors (Continued)
	5
	Aprox 14:30 – 15th January 2005
	Oliver Cabling
	After confirming with BAU that work can be commenced Oliver Cabling will connect the firewall connection to each of the service processor involved in the activity as per appendix D.


	

	6
	
	EMC TS
	EMC TS will send a Test email and dial home once the installation is complete

	


Section 3-3: Post checks

	Step
	Time
	Owner
	Details
	Comment



	1.
	When section 

3-2 is confirmed and completed. 15th January 2005
	Business As Usual
	BAU will confirm that all the service processors are manageable by each of the  4 new management workstations:

eusan-mgt1

eusan-mgt2

eusan-mgt3

eusan-mgt4


	 

	2
	Aprox 14:30 – 15th January 2005
	Oliver Cabling
	Oliver cabling will de-patch the connections to the laptop service processors.


	


Section 3-4: Post activity

	Step
	Time
	Owner
	Details
	Comments

	1
	When section 

3-3 is confirmed and completed. 15th January 2005
	BAU
	BAU will use the default admin password to create/check users.
	Please see appendix G

	2
	
	EMC TS
	EMC TS will set the Admin password back to the EMC default Admin password.
	


Item 4: Remediation of power supply cabling and labels- DMX 5R &6R:

Work number: 150105-2

Change control number: 05265282

Work co-ordinator: Paul Haynes

Date: 

15th of January 2005

Location:
RDC 1st floor

Conference Call Number: 0207 986 7934 (pin 7934)
Item 4: Section Checklist

Remediation of power supply cabling and labels- DMX 5R &6R

	Section
	Details
	Comments
	Sign Off

	4-1
	DMX5R
	Missing PDU termination - Work carried over to 22/01/05
	 



	4-2
	DMX6R
	Missing PDU termination - Work carried over to 22/01/05
	 

	4-3
	Breaker Confirmations
	Missing PDU termination - Work carried over to 22/01/05
	

	Item 4 completion Sign Off: To be returned to BAU on completion.

Member of: _____________________________ NAME: ___________________________________ Date: ___/___/____




Section 4-1: DMX5R 

Without interruption to service Data Centre staff assisted by ENC CS and Applied Engineering will transpose Aux A and Aux B power cables for DMX5R.located at RDC Level 1

	Step
	Time
	Owner
	Details

	1
	Start time:

14:00pm

15th January 2005
	Citigroup Electrician
	By means of the switch fitted to PDU turn off the power to a spare socket

	2
	
	Citigroup Electrician
	Plug in 63amp adapter into a currently spare supply

	3
	
	EMC CS
	Check DMX5R has green power lights for:

a. Main A

b. Aux B

c. Main B

d. Aux A

  

	4
	
	Citigroup Electrician
	By means of the switch fitted to PDU turn off the power to socket PDU 1/4/91RYB

	5
	
	EMC CS
	Check DMX5R has Amber power lights for:

a. Aux B 

And has green power lights for:

b. Main A

c. Main B

d. Aux A

	6
	
	Citigroup Electrician
	Move DMX Aux B cable from PDU 1/4/91RYB to the adapter in the spare socket

	7
	
	Citigroup Electrician
	Restore power to the spare socket

	8
	
	EMC CS
	Check DMX5R has green power lights for:

a. Main A

b. Aux B

c. Main B

d. Aux A

  

	9
	
	Citigroup Electrician
	By means of the switch fitted to PDU turn off the power to socket PDU 1/2/84RYB.

Note

The power to the vacant socket PDU 1/4/91RYB should still be off from 3 above.

	10
	
	EMC CS
	Check DMX5R has Amber power lights for:

a. Aux A

And has green power lights for:

b. Main A

c. Main B

d. Aux B

	11
	
	Citigroup Electrician
	Move DMX5R Aux A cable from PDU 1/2/84RYB to PDU 1/4/91RYB  .

	12
	
	Citigroup Electrician
	Restore power to PDU 1/4/91RYB

	13
	
	EMC CS
	Check DMX5R has green power lights for:

a. Main A

b. Aux B

c. Main B

d. Aux A



	14
	
	Citigroup Electrician
	By means of the switch fitted to PDU turn off the power to the spare socket

Note

The power to the vacant socket PDU 1/2/84RYB should still be off from 8 above.

	15
	
	EMC CS
	Check DMX5R has Amber power lights for:

e. Aux B 

And has green power lights for:

f. Main A

g. Main B

h. Aux A

	16
	
	Citigroup Electrician
	Move DMX5R Aux B cable from the spare socket to PDU 1/2/84RYB

	17
	
	Citigroup Electrician
	Restore power to PDU 1/2/84RYB

	18
	
	EMC CS
	Check DMX5R has green power lights for:

e. Main A

f. Aux B

g. Main B

h. Aux A

  

	19
	
	
	DMX5R power feeds should now be rectified


Section 4-2: DMX6R

Without interruption to service Data Centre staff assisted by ENC CS and Applied Engineering will transpose Aux A and Aux B power cables for DMX6R.located at RDC Level 1
	Step
	Time
	Owner
	Details

	1.
	Start time:

14:00pm

15th January 2005
	Citigroup Electrician
	By means of the switch fitted to PDU turn off the power to a spare socket

	
	
	Citigroup Electrician
	Plug in 63amp adapter into a currently spare supply

	2.
	
	EMC CS
	Check DMX6R has green power lights for:

e. Main A

f. Aux B

g. Main B

h. Aux A

  

	3.
	
	Citigroup Electrician
	By means of the switch fitted to PDU turn off the power to socket PDU 1/2/82RYB

	4.
	
	EMC CS
	Check DMX6R has Amber power lights for:

i. Aux B 

And has green power lights for:

j. Main A

k. Main B

l. Aux A

	5.
	
	Citigroup Electrician
	Move DMX Aux B cable from PDU 1/2/82RYB to the adapter in the spare socket

	6.
	
	Citigroup Electrician
	Restore power to the spare socket



	7.
	
	EMC CS
	Check DMX6R has green power lights for:

i. Main A

j. Aux B

k. Main B

l. Aux A

  

	8.
	
	Citigroup Electrician
	By means of the switch fitted to PDU turn off the power to socket PDU 1/4/89RYB.

Note

The power to the vacant socket PDU 1/2/82RYB should still be off from 3 above.

	9.
	
	EMC CS
	Check DMX6R has Amber power lights for:

e. Aux A

And has green power lights for:

f. Main A

g. Main B

h. Aux B

	10.
	
	Citigroup Electrician
	Move DMX6R Aux A cable from PDU 1/4/89RYB to PDU 1/2/82RYB  .

	11.
	
	Citigroup Electrician
	Restore power to PDU 1/2/82RYB

	12.
	
	EMC CS
	Check DMX6R has green power lights for:

e. Main A

f. Aux B

g. Main B

h. Aux A



	13.
	
	Citigroup Electrician
	By means of the switch fitted to PDU turn off the power to the spare socket

Note

The power to the vacant socket PDU 1/4/89RYBshould still be off from 8 above.

	14.
	
	EMC CS
	Check DMX6R has Amber power lights for:

m. Aux B 

And has green power lights for:

n. Main A

o. Main B

p. Aux A

	15.
	
	Citigroup Electrician
	Move DMX6R Aux B cable from the spare socket to PDU 1/4/89RYB

	16
	
	Citigroup Electrician
	Restore power to PDU 1/4/89RYB

	17.
	
	EMC CS
	Check DMX6R has green power lights for:

m. Main A

n. Aux B

o. Main B

p. Aux A

  

	18.
	
	
	DMX6R power feeds should now be rectified


	Section 4-3: Breaker confirmations (RDC)

	
	
	
	

	SYMM
	SYMM Connection
	Power Breaker
	Confirm (Y/N)

	5R
	Main A
	1/2/81RYB
	 

	5R
	Main B
	1/4/24RYB
	 

	5R
	Aux A
	1/4/91RYB
	 

	5R
	Aux B
	1/2/84RYB
	 

	6R
	Main A
	1/4/90RYB
	 

	6R
	Main B
	1/2/83RYB
	 

	6R
	Aux A
	1/2/82RYB
	 

	6R
	Aux B
	1/4/89RYB
	 

	7R
	Main A
	1/4/96RYB
	 

	7R
	Main B
	1/2/79RYB
	 

	7R
	Aux A
	1/2/78RYB
	 

	7R
	Aux B
	1/4/95RYB
	 

	8R
	Main A
	1/2/88RYB
	 

	8R
	Main B
	1/4/85RYB
	 

	8R
	Aux A
	1/4/78RYB
	 

	8R
	Aux B
	1/2/87RYB
	 

	9R
	Main A
	4/8/2RYB
	 

	9R
	Main B
	4/6/2RYB
	 

	9R
	Aux A
	4/6/1RYB
	 

	9R
	Aux B
	4/8/1RYB
	 

	10R
	Main A
	4/7/2RYB
	 

	10R
	Main B
	4/5/2RYB
	 

	10R
	Aux A
	4/5/1RYB
	 

	10R
	Aux B
	4/7/1RYB
	 

	11R
	Main A
	4/8/5 RYB 
	 

	11R
	Main B
	 4/6/4 RYB
	 

	11R
	Aux A
	 4/6/3 RYB
	 

	11R
	Aux B
	 4/8/6 RYB
	 


Appendix A: Contact details


Work Co-ordinator
Graham Rodell 



Mobile: 07813602734



Email: graham.rodell@citigroup.com
BAU: 



Paul Haynes

DMX5/6R Power

Mobile: 07796307355

Supply remediation

Email: mailto:paul.haynes@citigroup.com
BAU: Other


David Coles





Mobile: 07934807687





E-mail: mailto:david.peter.coles@citigroup.com
Oliver Cabling CGC/RDC:
Carl Williams



Mobile: 07966466956



Email: mailto:Carl.Patrick.Williams@citigroup.com
EMC CS


Chris Hankinson





Mobile: 07710362871





Email:mailto:hankinson_chris@emc.com
Contact details (continued)
EMC TS:


Tahir Shahid







Mobile: 07802241372





E-mail: mailto:shahid_tahir@emc.com 


EMC SAM:


Paul Belcher





Mobile: 07730781388





E-Mail: Belcher_Paul@emc.com
EMC Project Manager
Gary Battersby





Mobile: 07747765660





E-mail: mailto:Battersby_Gary@emc.com
EMC CE:


Patrick Caborn





Mobile: 07801214303






E-mail: mailto:caborn_patrick@emc.com
CRS:



67788 – Out of hours this will re-direct to on-call engineer

BMS (RDC Only)

69965

COMMAND CENTRE: 020 7986 2020

Appendix B: Cabinet information - RDC

	Red Fabric

	Switch
	Switch serial number
	Location
	Connectrix cab
	Fabric
	Model
	Domain ID
	Firmware
	Type
	Hub Port

	1R
	MC5FJ01954
	RDC1
	BX04
	MC5CN04024
	RED
	ED-64M
	2
	6.01.00.18
	Core
	BX04 - Hub 01/02

	3R
	MC5FJ01953
	RDC1
	BX04
	MC5CN04024
	RED
	ED-64M
	28
	6.01.00.18
	Edge
	BX04 - Hub 04/05

	5R
	MC5FJ07237
	RDC1
	BX04
	MC5CN04024
	RED
	ED-64M
	27
	6.01.00.18
	Edge
	BX04 - Hub 07/08

	7R
	MC5FJ01858
	RDC4
	BU18
	MC5TN01560
	RED
	ED-140M
	26
	6.01.00.18
	Edge
	BX04 - Hub 24

	9R
	MC5FJ01292
	RDC1
	BX04
	MC5CN04024
	RED
	RD-64M
	22
	6.01.00.18
	Edge
	BX04 - Hub 09/10

	11R
	MC5CI01485
	RDC1
	BX11
	MC5N07128
	RED
	ED-140M
	3
	6.01.00.18
	Core
	BX04 - Hub 17/18

	13R
	MC5CI01684
	RDC1
	BX11
	MC5N07128
	RED
	ED-140M
	21
	6.01.00.18
	Edge
	BX04 - Hub 15/16

	15R
	MC5IN02551
	RDC4
	M01
	MC5TN01559
	RED
	ED-140M
	4
	6.01.00.18
	Core
	BU18 - Hub 

	17R
	MC5FJ01848
	RDC3
	Z02
	MC5CN04014
	RED
	ED-64M
	20
	6.01.00.18
	Edge
	BX04 - Hub 

	19R
	MC5FJ01848
	RDC1
	BX11
	MC5N07128
	RED
	ED-140M
	19
	6.01.00.18
	Edge
	BX04 - Hub 13/14

	Green RDF Fabric

	Switch
	Switch serial number
	Location
	Connectrix cab
	Fabric
	Model
	Domain ID
	Firmware
	Type
	Hub Port

	rdfsw91r
	MC5FJ21148
	RDC1
	BX17
	MC5TN01413
	Green
	ED-64M
	3
	6.01.00.18
	rdf
	BX17 - Hub 07/08

	rdfsw93r
	MC5FJ21147
	RDC4
	M02
	MC5TN01412
	Green
	ED-64M
	7
	6.01.00.18
	rdf
	BX17 - Hub 24

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	Blue Fabric

	Switch
	Switch serial number
	Location
	Connectrix cab
	Fabric
	Model
	Domain ID
	Firmware
	Type
	Hub Port

	2R
	MC5FJ02061
	RDC1
	BX40
	MC5CN04016
	Blue
	ED-64M
	2
	6.01.00.18
	Core
	BX40 - Hub 01/02

	4R
	MC5FJ02060
	RDC1
	BX40
	MC5CN04016
	Blue
	ED-64M
	28
	6.01.00.18
	Edge
	BX40 - Hub 04/05

	6R
	MC5FJ07236
	RDC1
	BX40
	MC5CN04016
	Blue
	ED-64M
	27
	6.01.00.18
	Edge
	BX40 - Hub 07/08

	8R
	MC5FJ02020
	RDC4
	BU26
	MC5TN01562
	Blue
	ED-140M
	26
	6.01.00.18
	Edge
	BX40 - Hub 24

	10R
	MC5FJ01297
	RDC1
	BX40
	MC5CN04016
	Blue
	RD-64M
	22
	6.01.00.18
	Edge
	BX40 - Hub 09/10

	12R
	MC5CI01482
	RDC1
	BX34
	MC5CN06898
	Blue
	ED-140M
	3
	6.01.00.18
	Core
	BX40 - Hub 17/18

	14R
	MC5CI01585
	RDC1
	BX34
	MC5CN06898
	Blue
	ED-140M
	21
	6.01.00.18
	Edge
	BX40 - Hub 13/16

	16R
	MC5IN02566
	RDC4
	M46
	MC5TN01563
	Blue
	ED-140M
	4
	6.01.00.18
	Core
	BU26 - Hub 

	18R
	MC5FJ02020
	RDC3
	Z44
	MC5CN04016
	Blue
	ED-64M
	20
	6.01.00.18
	Edge
	 

	20R
	MC5IN02562
	RDC1
	BX34
	MC5CN06898
	Blue
	ED-140M
	19
	6.01.00.18
	Edge
	BX40 - Hub 14/15

	Black RDF Fabric

	Switch
	Switch serial number
	Location
	Connectrix cab
	Fabric
	Model
	Domain ID
	Firmware
	Type
	Hub Port

	rdfsw91r
	MC5FJ21144
	RDC1
	BX33
	MC5TN01409
	Black
	ED-64M
	4
	6.01.00.18
	rdf
	BX33 - Hub 07/08

	rdfsw93r
	MC5FJ21146
	RDC4
	M45
	MC5TN01411
	Black
	ED-64M
	8
	6.01.00.18
	rdf
	BX33 - Hub 24


	DMX/SYMM/CLARION

	DMX/ SYMM
	Serial number
	Location
	Model
	Microcode
	Software
	Modem Details

	1R
	CK284700428
	RDC1
	BX42-44
	8730
	5567.53.30
	SYMMIP
	 

	2R
	CK284701227
	RDC1
	BX01-03
	8730
	5567.53.30
	SYMMIP
	 

	3R
	CK284701079
	RDC1
	BX06-08
	8730
	5567.53.30
	SYMMIP
	 

	4R
	CK284700466
	RDC1
	BX36-38
	8730
	5567.53.30
	SYMMIP
	 

	5R
	SA287750107
	RDC1
	BX10
	DMX2000
	5670.73.69
	SYMMIP
	 

	6R
	SA287750096
	RDC1
	BX19
	DMX2000
	5670.73.69
	SYMMIP
	 

	7R
	SA287750200
	RDC1
	BX22
	DMX2000
	5670.73.69
	SYMMIP
	 

	8R
	SA287750442
	RDC1
	BX13
	DMX2000
	5670.73.69
	SYMMIP
	 

	CX1R
	MSL00040900021
	RDC1
	BX35
	CX600
	?
	?
	 

	9R
	CK287890275
	RDC4
	C04
	DMX3000
	5670.73.69
	SYMMIP
	 

	10R
	CK287890300
	RDC4
	C42
	DMX3000
	5670.73.69
	SYMMIP
	 

	11R
	CK287890293
	RDC4
	F04
	DMX3000
	5670.73.69
	SYMMIP
	 


Appendix B: Cabinet information - CGC

	Red Fabric

	Switch
	Switch serial number
	Location
	Connectrix cab
	Fabric
	Model
	Domain ID
	Firmware
	Type
	Hub Port

	1
	MC5FJ01158
	CGC1
	60AN
	MC5CN03485
	RED
	ED-64M
	1
	6.01.00.18
	Core
	60AN Hub 01/02

	3
	MC5IN02560
	CGC2
	CA95
	MC5TN01558
	RED
	ED-140M
	18
	6.01.00.18
	Edge
	CA95 Hub 07/08

	5
	MC5FJ01267
	CGC1
	60AN
	MC5CN03485
	RED
	ED-64M
	30
	6.01.00.18
	Edge
	60AN Hub 07/08

	7
	MC5FJ01159
	CGC1
	60AN
	MC5CN03485
	RED
	ED-64M
	29
	6.01.00.18
	Edge
	60AN Hub 04/05

	9
	MC5FJ07225
	CGC2
	BW100
	MC5CN03485
	RED
	ED-64M
	25
	6.01.00.18
	Edge
	BW100 Hub 01/02

	11
	MC5FJ01673
	CGC2
	BW100
	MC5CN04635
	RED
	ED-64M
	24
	6.01.00.18
	Edge
	BW100 Hub 03/04

	13
	MC51N01268
	CGC2
	BW100
	MC5CN04635
	RED
	ED-140M
	23
	6.01.00.18
	Core
	BW100 Hub 05/06

	15
	MC5CIN01483
	CGC2
	BW101
	MC5CN07127
	RED
	ED-140M
	20
	6.01.00.18
	Edge
	BW100 Hub 07/20

	Green RDF Fabric

	Switch
	Switch serial number
	Location
	Connectrix cab
	Fabric
	Model
	Domain ID
	Firmware
	Type
	Hub Port

	rdfsw91C
	MC5FJ21145
	CGC1
	59AN
	MC5TN01410
	Green
	ED-64M
	1
	6.01.00.18
	RDF
	59AN Hub 07/08

	rdfsw93C
	MC5FJ21149
	CGC2
	CA96
	MC5TN01414
	Green
	ED-64M
	5
	6.01.00.18
	RDF
	CA96 Hub 07/08

	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	

	Blue Fabric

	Switch
	Switch serial number
	Location
	Connectrix cab
	Fabric
	Model
	Domain ID
	Firmware
	Type
	Hub Port

	2
	MC5FJ01182
	CGC1
	71CF
	MC5CN03484
	Blue
	ED-64M
	1
	6.01.00.18
	Core
	71CF Hub 01/02

	4
	MC5IN02580
	CGC2
	CB15
	MC5TN01561
	Blue
	ED-140M
	18
	6.01.00.18
	Edge
	CB15 Hub 07/08

	6
	MC5FJ01308
	CGC1
	71CF
	MC5CN03484
	Blue
	ED-64M
	30
	6.01.00.18
	Edge
	71CF Hub 07/08

	8
	MC5FJ01183
	CGC1
	71CF
	MC5CN03484
	Blue
	ED-64M
	29
	6.01.00.18
	Edge
	71CF Hub 04/05

	10
	MC5FJ07208
	CGC2
	CB05
	MC5CN04634
	Blue
	ED-64M
	25
	6.01.00.18
	Edge
	CB05 Hub 01/02

	12
	MC5FJ09611
	CGC2
	CB05
	MC5CN04634
	Blue
	ED-64M
	24
	6.01.00.18
	Edge
	CB05 Hub 03/04

	14
	MCF1N01267
	CGC2
	CB05
	MC5CN04634
	Blue
	ED-140M
	23
	6.01.00.18
	Core
	CB05 Hub 07/08

	16
	MC5IN01484
	CGC2
	CB06
	MC5TN06731
	Blue
	ED-140M
	20
	6.01.00.18
	Edge
	CB05 Hub 13/14

	Black RDF Fabric

	Switch
	Switch serial number
	Location
	 
	Connectrix cab
	Fabric
	Model
	Domain ID
	Firmware
	Type
	Hub Port

	rdfsw92C
	MC5FJ21143
	CGC1
	70CF
	MC5TN01408
	Black
	ED-64M
	2
	6.01.00.18
	RDF
	70CF Hub 07/08

	rdfsw94C
	MC5FJ21150
	CGC2
	CB14
	MC5TN01415
	Black
	ED-64M
	6
	6.01.00.18
	RDf
	CB14 Hub 07/08


	DMX/SYMM/CLARION

	DMX/ SYMM
	Serial number
	Location
	Model
	Microcode
	Software
	Modem Details

	1C
	CK284700679
	CGC1
	69AZ
	8730
	5567.53.30
	SYMMIP
	 

	2C
	CK284700995
	CGC1
	56AZ
	8730
	5567.53.30
	SYMMIP
	 

	3C
	CK284701078
	CGC1
	67BN
	8730
	5567.53.30
	SYMMIP
	 

	4C
	CK284700214
	CGC2
	BW98
	8730
	5567.53.30
	SYMMIP
	 

	5C
	SA287750129
	CGC2
	CB09
	DMX2000
	5670.73.69
	SYMMIP
	 

	6C
	SA287750125
	CGC2
	BW94
	DMX2000
	5670.73.69
	SYMMIP
	 

	7C
	SA287750122
	CGC2
	CB12
	DMX2000
	5670.73.69
	SYMMIP
	 

	8C
	SA287750383
	CGC2
	BW92
	DMX2000
	5670.73.69
	SYMMIP
	 

	9C
	CK287890296
	CGC2
	BC06
	DMX3000
	5670.73.69
	SYMMIP
	 

	10C
	CK287890294
	CGC2
	BH100
	DMX3000
	5670.73.69
	SYMMIP
	 

	11C
	CK287890298
	CGC2
	AZ07
	DMX3000
	5670.73.69
	SYMMIP
	 

	CX1C
	MSL00040800040
	CGC2
	CA101
	CX600
	 
	 
	 


Appendix C:
	
	
	
	
	

	Command
	Test
	Actual Result
	Expected result
	Additional Comments

	EFCM ConnectrixManager
	
	
	

	
	
	
	
	

	on eusan-mgt1
	Start and login to CGC Red Fabric
	Connectrix Manager starts, login works and switches can be viewed

	
	Start and login to CGC Blue Fabric
	Connectrix Manager starts, login works and switches can be viewed

	
	Start and login to CGC Green Fabric
	Connectrix Manager starts, login works and switches can be viewed

	
	Start and login to CGC Black Fabric
	Connectrix Manager starts, login works and switches can be viewed

	
	
	
	
	

	on eusan-mgt2
	Start and login to RDC Red Fabric
	Connectrix Manager starts, login works and switches can be viewed

	
	Start and login to RDC Blue Fabric
	Connectrix Manager starts, login works and switches can be viewed

	
	Start and login to RDF Green Fabric
	Connectrix Manager starts, login works and switches can be viewed

	
	Start and login to RDC Black Fabric
	Connectrix Manager starts, login works and switches can be viewed

	
	
	
	
	

	on eusan-mgt3
	Start and login to CGC Red Fabric
	Connectrix Manager starts, login works and switches can be viewed

	
	Start and login to CGC Blue Fabric
	Connectrix Manager starts, login works and switches can be viewed

	
	Start and login to CGC Green Fabric
	Connectrix Manager starts, login works and switches can be viewed

	
	Start and login to CGC Black Fabric
	Connectrix Manager starts, login works and switches can be viewed

	
	
	
	
	

	on eusan-mgt4
	Start and login to RDC Red Fabric
	Connectrix Manager starts, login works and switches can be viewed

	
	Start and login to RDC Blue Fabric
	Connectrix Manager starts, login works and switches can be viewed

	
	Start and login to RDF Green Fabric
	Connectrix Manager starts, login works and switches can be viewed

	
	Start and login to RDC Black Fabric
	Connectrix Manager starts, login works and switches can be viewed

	
	
	
	
	

	
	Simultaneously run two sessions on one server to same SP
	Connectrix Manager starts, login works and switches can be viewed

	
	Simultaneously run two sessions on one server to different SP
	Connectrix Manager starts, login works and switches can be viewed

	
	
	
	
	

	
	Simultaneously run two sessions to single SP on different servers
	Connectrix Manager starts, login works and switches can be viewed

	
	
	

	
	
	
	
	

	E-mail
	Send test event from CGC Red Fabric
	test event e-mail is received by members of *gt uk san auto

	
	Send test event from CGC Blue Fabric
	test event e-mail is received by members of *gt uk san auto

	
	Send test event from RDC Red Fabric
	test event e-mail is received by members of *gt uk san auto

	
	Send test event from RDC Blue Fabric
	test event e-mail is received by members of *gt uk san auto

	
	Send test event from CGC Green Fabric
	test event e-mail is received by members of *gt uk san auto

	
	Send test event from CGC Black Fabric
	test event e-mail is received by members of *gt uk san auto

	
	Send test event from RDC Green Fabric
	test event e-mail is received by members of *gt uk san auto

	
	Send test event from RDC Black Fabric
	test event e-mail is received by members of *gt uk san auto


Appendix D:

	
	Firewall Rules
	
	
	

	
	
	
	
	
	

	CGC
	
	
	
	
	CSP = Connectrix Service Processor

	
	
	
	
	
	

	Source Name
	Source Address
	Destination Name
	Destination Address
	Ports(s)
	Comments

	All CSP CGC
	
	mailhub-vip.ny.ssmb.com
	162.124.146.243
	smtp (25)
	Outgoing alert Emails from CSP

	All CSP CGC
	
	All CGC Storage Mgr Serv
	
	1024-65535
	Outgoing Connectrix Manager traffic

	All CGC Storage Mgr Serv
	
	All CSP CGC
	
	1024-65535
	Incomming Connectrix Manager traffic

	All CGC Storage Mgr Serv
	
	All CSP CGC
	
	80
	Client side application updates

	All CGC Storage Mgr Serv
	
	All CSP CGC
	
	ftp (21)
	Client side application updates

	All CSP CGC
	
	All CGC Storage Mgr Serv
	
	575
	Connectrix Manager event notification to client

	All CGC Storage Mgr Serv
	
	All CSP CGC
	
	111, 3127, 4023
	ESN Manager & FibreZone bridge communications

	
	
	
	
	
	

	
	
	
	
	
	

	RDC
	
	
	
	
	

	
	
	
	
	
	

	Source Name
	Source Address
	Destination Name
	Destination Address
	Ports(s)
	Comments

	All CSP RDC
	
	mailhub-vip.ny.ssmb.com
	162.124.146.243
	smtp (25)
	Outgoing alert Emails from CSP

	All CSP RDC
	
	All RDC Storage Mgr Serv
	
	1024-65535
	Outgoing Connectrix Manager traffic

	All RDC Storage Mgr Serv
	
	All CSP RDC
	
	1024-65535
	Incomming Connectrix Manager traffic

	All RDC Storage Mgr Serv
	
	All CSP RDC
	
	80
	Client side application updates

	All RDC Storage Mgr Serv
	
	All CSP RDC
	
	ftp (21)
	Client side application updates

	All CSP CGC
	
	All CGC Storage Mgr Serv
	
	575
	Connectrix Manager event notification to client

	All RDC Storage Mgr Serv
	
	All CSP RDC
	
	111, 3127, 4023
	ESN Manager & FibreZone bridge communications

	
	
	
	
	
	

	
	
	IP Addresses
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	RDC
	
	
	
	
	

	Management Workstation
	IP Address
	CEP Location
	Cisco
	Card/Port
	Vlan #, Netmask, Default Gateway

	sanuk03-pub
	169.186.201.26
	
	
	
	

	eusan-mgt2
	169.186.223.81
	RDC Floor 1
	
	
	

	eusan-mgt4
	169.186.223.170
	RDC Floor 1
	
	
	

	
	
	
	
	
	

	RDC CSP Floor/Location
	
	
	
	
	

	rdcblackfabric L4/M45
	169.186.192.196
	4th AX42
	srdcfwe14
	3/6
	43, 255.255.255.192, 169.186.192.193

	rdcbluefabric L4/M46
	169.186.192.197
	4th AX2
	srdcfwe13
	3/7
	43, 255.255.255.192, 169.186.192.193

	rdcblackstdby L1/BX33
	169.186.192.68
	1st BL02
	srdcfwe09
	3/37
	10, 255.255.255.192, 169.186.192.65

	rdcbluestdby L1/BX40
	169.186.192.69
	1st BL32
	srdcfwe10
	3/38
	10, 255.255.255.192, 169.186.192.65

	Vlan 8 <-> Vlan 53
	
	
	
	
	

	Vlan 9 <-> Vlan 54
	
	
	
	
	

	
	
	
	
	
	

	CGC
	
	
	
	
	

	Management Workstation
	IP Address
	Location
	Cisco
	Card/Port
	Vlan #, Netmask, Default Gateway

	sanuk01-pub
	169.186.146.103
	
	
	
	

	eusan-mgt1
	169.183.26.108
	CGC2 Floor 3 
	
	
	

	eusan-mgt3
	169.183.27.90
	CGC2 Floor 3 
	
	
	

	
	
	
	
	
	

	CGC CSP
	
	
	
	
	

	cgcblackfabric L2/CB14
	169.186.141.196
	cgc2 AB68
	sol2fwe02
	4/9
	54, 255.255.255.192, 169.186.141.193

	cgcbluefabric L2/CB15
	169.186.141.197
	cgc2 AB51
	sol2fwe01
	4/10
	54, 255.255.255.192, 169.186.141.193

	cgcblackstdby TR1/TR2 70CF
	169.186.141.68
	cgc1 TR3 40DB
	sol1fwe15
	4/8
	9, 255.255.255.192, 169.186.141.65

	cgcbluestdby TR1/TR2 71CF
	169.186.141.69
	cgc1 TR4 81CW
	sol1fwe16
	4/9
	9, 255.255.255.192, 169.186.141.65

	Vlan 9 <-> Vlan 42

Vlan 10 <-> Vlan 43


	
	
	
	
	


	
	
	
	
	
	


Appendix E:
Below are the from address strings for the SP config.properties file. It should be noted that the work currently being undertaken is the first of a 3-phase implementation of a LAN design. 

For RDC

Blue Fabric

EmailFromAddress=Connectrix-service.RDC.BLUE@rdcbluefabric.eur.nsroot.net
Black Fabric

mailto:EmailFromAddress=Connectrix-service.RDC.BLACK@rdcblackfabric.eur.nsroot.net
For CGC

Blue Fabric

EmailFromAddress=Connectrix-service.CGC.BLUE@cgcbluefabric.eur.nsroot.net
Note

Should emails not be received due to non-name resolution by DNS, the name after @ should be deleted and the IP address 162.124.146.243, for example:

 EmailFromAddress=Connectrix-service.RDC.BLACK@162.124.146.243
Appendix F:

Item: 1-1 

This work has been carried forward from CR-5089731

Below are the devices that are to be used for the create pairs.

The file for the command is eusan-mgt1:/var/tmp/symconfigure/flex_create_pair

The command to create the dynamic srdf pairs should be run from eusan-mgt1 & is:-

 symrdf  createpair –file flex_create_pair –sid 122 –rdfg1 –type RDF2 –establish.
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Items: 1-2

Ports to be amended on switches in CGC:

	DMX 7C
	WWN
	Switch 93C port
	Switch 94C port
	Switch 13C port
	Switch 14C port

	4cA
	5006048C49ADFA83
	 
	 
	58
	 

	4dA
	5006048C49ADFA93
	17
	 
	 
	 

	5aA
	5006048449ADFA84
	 
	 
	86
	 

	5bA
	5006048449ADFA94
	 
	 
	88
	 

	5cA
	5006048C49ADFA84
	 
	 
	92
	 

	5dA
	5006048C49ADFA94
	13
	 
	 
	 

	12aA
	5006048449ADFA8B
	 
	 
	 
	88

	12bA
	5006048449ADFA9B
	 
	 
	 
	86

	12cA
	5006048C49ADFA8B
	 
	 
	 
	92

	12dA
	5006048C49ADFA9B
	 
	13
	 
	 

	13cA
	5006048C49ADFA8C
	 
	 
	 
	58

	13dA
	5006048C49ADFA9C
	 
	17
	 
	 


The FA’s that are highlighted in Bold/red are for symm 122 at CGC that are currently offline.

Taken from as fitted document (CR-5089731) from 4/12/04.

Ports should be unblocked & then nicknamed using convention –eg:- SYMM7-122-5aA.
Appendix G:

If the data cannot be transferred on to the new service processors the following accounts will need to be added:

sa47183 - Salauddin Ahmed - Admin

cc83851 - Chris Calyton - Operator

sh93900 - Stephen Hopkins - Operator

cw93752 - Carl Woolward - Admin

gr40692 - Graham Rodell - Admin

ph47197 - Paul Haynes - Admin

md25176 - Jadev Dad - Admin

cb21507 - Colin Bradley - Operator

dc91175 - David Coles - Admin
Drawings/Diagrams

The attached drawings are ONLY intended for reference, and are to be only used in conjunction with this document.

CGC1&2 Topology_v0.1 – A reflection of the CGC1/2 Cabinets, Switches, Current service processors and how they are all interlinked.

CGC1&2 Topology_v0.2  – A reflection of the CGC1/2 Cabinets, Switches, Service processors after they have been relocated to 1U processors and how they are all interlinked.

RDC Blue/Black Topology_v0.1 - A reflection of the RDC Blue/Black Cabinets, Switches, Current service processors and how they are all interlinked.

RDC Blue/Black Topology_v0.2 – A reflection of the RDC Blue/Black Cabinets, Switches, Service processors after they have been relocated to 1U processors and how they are all interlinked.

Drawings/Diagrams – CGC1&2 topology_V0.1
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Drawings/Diagrams – CGC1&2 topology_V0.2
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Drawings/Diagrams – RDC Blue/Black topology_V0.1
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Drawings/Diagrams – RDC Blue/Black topology_V0.2
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